## All Data (by sample)
Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event |  |  |  |  | Additional Comments
Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM
No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb
1 | 2017-08-23 | Sample 1 | 4B tank | Pre-clarified w/ PAC then chlorinated | A | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 1.42 | 1.65 | 0.23 |  | 60 | First day using charcoal stuff to ensure boiling water step, so earlier grab sample data (8 samples) discarded
2 | 2017-08-23 | Sample 2 | 7B inflow | Post-aeration | A | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 1.62 | 1.89 | 0.27 |  | 41.3333 | Post-aeration samples taken at arms length down into receiving tank, as far as we can reach below the aerator outlet
3 | 2017-08-23 | Sample 3 | 4A tank | Alum and chlorination at same time | B | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 0.8 | 1.11 | 0.31 |  | 95.98
4 | 2017-08-23 | Sample 4 | 8A inflow | Post-aeration | B | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 |  |  |  |  | 90 | Water wasted before FRC could be done
5 | 2017-08-23 | Sample B | Deionized water blank | [5 empty] | 2017-08-23 11:00
6 | 2017-08-24 | Aug24-1 | 6B tank | Pre-clarified w/ PAC then chlorinated | C | 2017-08-24 10:02 | 2017-08-24 10:38 | n/a | 2017-08-24 10:52 | 0:50 | 1.68 | 1.9 | 0.22 |  | 46
7 | 2017-08-24 | Aug24-2 | 8B inflow | Post-aeration | C | 2017-08-24 10:02 | 2017-08-24 10:38 | n/a | 2017-08-24 10:52 | 0:50 | 1.77 | 1.89 | 0.12 |  | 41
8 | 2017-08-24 | Aug24-3 | 8B inflow | Stored overnight | C | 2017-08-24 10:02 | 2017-08-24 10:40 | 2017-08-24 10:45 | 2017-08-25 10:33 | 24:31 | 0.81 | 0.88 | 0.07 | 7.2 | 63 | Filled 1.5L PET water bottle with a jug from arms length down aeration flow, right up to lip to minimize airspace, stored under lab bench in dark place
9 | 2017-08-24 | Aug24-4B | Deionized water blank | [5 empty] | 2017-08-24 10:52
10 | 2017-08-24 | Aug24-5 | 4B tank | Pre-clarified w/ PAC then chlorinated | D | 2017-08-24 12:15 | 2017-08-24 12:45 | n/a | 2017-08-24 12:52 | 0:37 | 1.86 | 2 | 0.14 |  | 36
11 | 2017-08-24 | Aug24-6 | 9B inflow | Post-aeration | D | 2017-08-24 12:15 | 2017-08-24 12:46 | n/a | 2017-08-24 12:53 | 0:38 | 1.99 | 2.07 | 0.08 |  | 30
12 | 2017-08-24 | Aug24-7 | 9B inflow | Stored overnight | D | 2017-08-24 12:15 | 2017-08-24 12:49 | 2017-08-24 12:52 | 2017-08-25 10:36 | 22:21 | 0.74 | 0.83 | 0.09 | 7.27 | 114 | THM reading may be error arising due to smudging from wet and dirty glass cleaning cloth. This error is likely an overestimate because smudging will increase absorbance and create a falsely high reading.
13 | 2017-08-24 | Aug24-8B | Deionized water blank | [5 empty] | 2017-08-24 12:53
14 | 2017-08-25 | Aug25-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | E | 2017-08-25 09:40 | 2017-08-25 10:14 | n/a | 2017-08-25 10:38 | 0:58 | 1.45 | 1.63 | 0.18 | 7.16 | 46.5 | Multiple readings taken and averaged with 1-2 minutes between readings; one anomolous reading (134 ppb) discarded as likely due to a smudge on glass which did not persist with subsequent readings
15 | 2017-08-25 | Aug25-2 | 7B inflow | Post-aeration | E | 2017-08-25 09:40 | 2017-08-25 10:16 | n/a | 2017-08-25 10:40 | 1:00 | 1.42 | 1.57 | 0.15 | 7.25 | 68.25 | Multiple readings taken and averaged with 1-2 minutes between readings; one anomolous reading (96 ppb) discarded as likely due to a smudge on glass which did not persist with subsequent readings
16 | 2017-08-25 | Aug25-3 | 7B inflow | Stored overnight | E | 2017-08-25 09:40 | 2017-08-25 10:19 | 2017-08-25 10:25 | 2017-08-26 14:26 | 28:46 | 0.68 | 0.84 | 0.16 | 0.16 | 70 | *
17 | 2017-08-25 | Aug25-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | F | 2017-08-25 09:17 | 2017-08-25 10:21 | n/a | 2017-08-25 10:40 | 1:23 | 3.08 | 3.16 | 0.08 | 7.23 | 63.6667 | From now on, will take 3-5 THM readings with 1-2 minutes between and average the finding
18 | 2017-08-25 | Aug25-5 | 8B inflow | Post-aeration | F | 2017-08-25 09:17 | 2017-08-25 10:26 | n/a | 2017-08-25 10:40 | 1:23 | 3.16 | 3.27 | 0.11 | 7.28 | 56.5
19 | 2017-08-25 | Aug25-6 | 8B inflow | Stored overnight | F | 2017-08-25 09:17 | 2017-08-25 10:26 | 2017-08-25 10:29 | 2017-08-26 14:23 | 29:06 | 2.25 | 2.45 | 0.2 | 7.05 | 85 | *With above, we see that the overnight THM production in related to the FRC levels as well
20 | 2017-08-25 | Aug25-7B | Deionized water blank | [5 empty] | 2017-08-25 10:40
21 | 2017-08-26 | Aug26-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | G | 2017-08-26 13:31 | 2017-08-26 14:02 | n/a | 2017-08-26 14:14 | 0:43 | 0.91 | 1.1 | 0.19 | 6.82 | 46.5
22 | 2017-08-26 | Aug26-2 | 7B inflow | Post-aeration | G | 2017-08-26 13:31 | 2017-08-26 14:02 | n/a | 2017-08-26 14:15 | 0:44 | 1.16 | 1.25 | 0.09 | 6.99 | 41.75
23 | 2017-08-26 | Aug26-3 | 7B inflow | Stored overnight | G | 2017-08-26 13:31 | 2017-08-26 14:03 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:31 | 0.44 | 0.6 | 0.16 | 7.08 | 62.6667
24 | 2017-08-26 | Aug26-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | H | 2017-08-26 13:03 | 2017-08-26 14:02 | n/a | 2017-08-26 14:17 | 1:14 | 1.29 | 1.5 | 0.21 | 7.01 | 49
25 | 2017-08-26 | Aug26-5 | 8B inflow | Post-aeration | H | 2017-08-26 13:03 | 2017-08-26 14:06 | n/a | 2017-08-26 14:20 | 1:17 | 1.35 | 1.48 | 0.13 | 7.26 | 45.75
26 | 2017-08-26 | Aug26-6 | 8B inflow | Stored overnight | H | 2017-08-26 13:03 | 2017-08-26 14:06 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:59 | 0.71 | 0.81 | 0.1 | 7.13 | 67.8333 | First THM reading at 14:21 and last one at 14:51, decreased by 5ppb by end -- this trend evident across readings, ppb declines with time up to -5 ppb
27 | 2017-08-27 | Aug27-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | I | 2017-08-27 12:08 | 2017-08-27 12:41 | n/a | 2017-08-27 13:08 | 1:00 | 1.35 | 1.4 | 0.05 | 7.16 | 41
28 | 2017-08-27 | Aug27-2 | 7B inflow | Post-aeration | I | 2017-08-27 12:08 | 2017-08-27 12:45 | n/a | 2017-08-27 13:08 | 1:00 | 1.48 | 1.69 | 0.21 | 6.77 |  | Sample spilled before THM reading so no data collected
29 | 2017-08-27 | Aug27-3 | 7B inflow | Stored overnight | I | 2017-08-27 12:08 | 2017-08-27 12:43 | 2017-08-27 12:50 | 2017-08-28 16:27 | 28:19 | 0.57 | 0.74 | 0.17 | 7.17 | 63.3333
30 | 2017-08-27 | Aug27-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | J | 2017-08-27 12:10 | 2017-08-27 12:46 | n/a | 2017-08-27 13:08 | 0:58 | 1.79 | 1.86 | 0.07 | 7.24 | 52.6667
31 | 2017-08-27 | Aug27-5 | 8B inflow | Post-aeration | J | 2017-08-27 12:10 | 2017-08-27 12:46 | n/a | 2017-08-27 13:08 | 0:58 | 1.67 | 1.8 | 0.13 | 7.33 | 54
32 | 2017-08-27 | Aug27-6 | 8B inflow | Stored overnight | J | 2017-08-27 12:10 | 2017-08-27 12:46 | 2017-08-27 12:50 | 2017-08-28 16:24 | 28:14 | 0.93 | 1.27 | 0.34 | 7.31 | 75.3333
33 | 2017-08-28 | Aug28-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | K | 2017-08-28 15:03 | 2017-08-28 15:53 | n/a | 2017-08-28 16:11 | 1:08 | 1.1 | 1.33 | 0.23 | 7.11 | 50.3333
34 | 2017-08-28 | Aug28-2 | 7B inflow | Post-aeration | K | 2017-08-28 15:03 | 2017-08-28 15:55 | n/a | 2017-08-28 16:13 | 1:10 | 1.23 | 1.36 | 0.13 | 7.21 | 46
35 | 2017-08-28 | Aug28-3 | 7B inflow | Stored overnight | K | 2017-08-28 15:03 | 2017-08-28 15:58 | 2017-08-28 16:08 | 2017-08-29 10:37 | 19:34 | 0.37 | 0.53 | 0.16 | 7.35 | 59.3333
36 | 2017-08-28 | Aug28-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | L | 2017-08-28 14:21 | 2017-08-28 16:01 | n/a | 2017-08-28 16:22 | 2:01 | 2.58 | 2.71 | 0.13 | 7.13 | 60.3333
37 | 2017-08-28 | Aug28-5 | 8B inflow | Post-aeration | L | 2017-08-28 14:21 | 2017-08-28 16:05 | n/a | 2017-08-28 16:22 | 2:01 | 2.83 | 2.91 | 0.08 | 7.17 | 45
38 | 2017-08-28 | Aug28-6 | 8B inflow | Stored overnight | L | 2017-08-28 14:21 | 2017-08-28 16:04 | 2017-08-28 16:08 | 2017-08-29 10:38 | 20:17 | 1.65 | 1.8 | 0.15 | 7.37 | 44.6667
39 | 2017-08-29 | Aug29-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | M | 2017-08-29 08:10 | 2017-08-29 10:19 | n/a | 2017-08-29 10:29 | 2:19 | 4.09 | 4.26 | 0.17 | 7.01 | 55.3333
40 | 2017-08-29 | Aug29-2 | 7B inflow | Post-aeration | M | 2017-08-29 08:10 | 2017-08-29 10:25 | n/a | 2017-08-29 10:29 | 2:19 | 4.02 | 4.16 | 0.14 | 7.06 | 51.6667
41 | 2017-08-29 | Aug29-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | N | 2017-08-29 08:05 | 2017-08-29 10:12 | n/a | 2017-08-29 10:33 | 2:28 | 1.58 | 1.73 | 0.15 | 7.16 | 48.6667
42 | 2017-08-29 | Aug29-5 | 8B inflow | Post-aeration | N | 2017-08-29 08:05 | 2017-08-29 10:16 | n/a | 2017-08-29 10:34 | 2:29 | 1.34 | 1.63 | 0.29 | 7.18 | 54.3333
43 | 2017-09-14 | Sept14-1 | 8B | Batch Cl2 post sedimentation + Storage | O | 2017-09-14 14:19 | 2017-09-14 16:08 | 2017-09-14 16:35 | 2017-09-15 16:05 | 25:46 | 0.23 | 0.34 | 0.11 | 7.09 | 117.3333
44 | 2017-09-14 | Sept14-2 | 8B | Batch Cl2 post sedimentation | O | 2017-09-14 14:29 | 2017-09-14 16:09 | n/a | 2017-09-14 17:15 | 2:46 | 1.43 | 1.52 | 0.09 | 7.16 | 83.6667
45 | 2017-09-14 | Sept14-3 | 7B | Batch Cl2 post sedimentation + Storage | P | 2017-09-14 13:27 | 2017-09-14 16:13 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:38 | 0.55 | 0.62 | 0.07 | 6.67 | 129
46 | 2017-09-14 | Sept14-4 | 7B | Batch Cl2 post sedimentation | P | 2017-09-14 13:27 | 2017-09-14 16:14 | n/a | 2017-09-14 17:15 | 3:48 | 1.58 | 1.69 | 0.11 | 7.28 | 89.3333
47 | 2017-09-14 | Sept14-5 | 9A | Batch Cl2 post sedimentation + Storage | Q | 2017-09-14 13:36 | 2017-09-14 16:21 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:29 | 0.48 | 0.62 | 0.14 | 7.09 | 133.6667
48 | 2017-09-14 | Sept14-6 | 9A | Batch Cl2 post sedimentation | Q | 2017-09-14 13:36 | 2017-09-14 16:21 | n/a | 2017-09-14 17:15 | 3:39 | 1.93 | 2.18 | 0.25 | 6.86 | 89
49 | 2017-09-14 | Sept14-7 | 1A | Cl2 & Sedimentation together (Pre-aeration) | R | 2017-09-14 12:04 | 2017-09-14 16:27 | n/a | 2017-09-14 17:15 | 5:11 | 0.05 | 0.07 | 0.02 | 6.87 | 229.3333 | Old system used, hand additonal of fluculant.
50 | 2017-09-14 | Sept14-8 | 8A | Cl2 & Sedimentation together (Post-aeration) | R | 2017-09-14 12:04 | 2017-09-14 16:32 | n/a | 2017-09-14 17:15 | 5:11 | 0.8 | 1.04 | 0.24 | 7.18 | 226.3333 | Old system used, hand additonal of fluculant.
51 | 2017-09-14 | Sept14-9 | 8A | Cl2 & Sedimentation together (Post-aeration & Storage) | R | 2017-09-14 12:04 | 2017-09-14 16:32 | 2017-09-14 16:35 | 2017-09-15 16:05 | 28:01 | 0.19 | 0.27 | 0.08 | 7.07 | 249 | Old system used, hand additonal of fluculant.
52 | 2017-09-15 | Sept15-1 | 4A | Cl2 & Sedimentation together | S | 2017-09-15 13:19 | 2017-09-15 15:12 | n/a | 2017-09-15 15:38 | 2:19 | 0.07 | 0.56 | 0.49 | 7.27 | 282.3333 | Old system used, hand additonal of fluculant.
53 | 2017-09-15 | Sept15-2 | 4A | Inflow post aerated | S | 2017-09-15 13:19 | 2017-09-15 15:13 | n/a | 2017-09-15 15:46 | 2:27 | 0.14 | 0.57 | 0.43 | 7.18 | 266.6667 | Old system used, hand additonal of fluculant.
54 | 2017-09-15 | Sept15-3 | 8B | Batch Cl2 post sedimentation | T | 2017-09-15 12:22 | 2017-09-15 15:18 | n/a | 2017-09-15 15:23 | 3:01 | 0.65 | 0.8 | 0.15 | 7.31 | 91
55 | 2017-09-19 | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight | U | 2017-09-18 17:02 | 2017-09-18 06:47 | 2017-09-18 06:47 | 2017-09-19 12:58 | 19:56 | 0.06 | 0.27 | 0.21 | 7.1 | 99
56 | 2017-09-19 | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight | V | 2017-09-18 18:41 | 2017-09-18 06:57 | 2017-09-18 06:57 | 2017-09-19 12:58 | 18:17 | 0.4 | 0.72 | 0.32 | 6.9 | 107.3333
57 | 2017-09-19 | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | W | 2017-09-18 18:18 | 2017-09-18 07:03 | 2017-09-18 07:03 | 2017-09-19 12:58 | 18:40 | 0.07 | 0.27 | 0.2 | 7.2 | 204 | Old system used, hand additonal of fluculant.
58 | 2017-09-19 | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | X | 2017-09-18 10:00 | 2017-09-18 12:16 | 2017-09-18 12:16 | 2017-09-19 12:58 | 26:58 | 0.74 | 0.9 | 0.16 | 7.5 | 93
59 | 2017-09-19 | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | Y | 2017-09-18 11:05 | 2017-09-18 12:18 | 2017-09-18 12:18 | 2017-09-19 12:58 | 25:53 | 0.54 | 0.73 | 0.19 | 7.3 | 201 | Old system used, hand additonal of fluculant.
60 | 2017-09-19 | Sept19-06 | 9A | Batch Cl2 post sedimentation. | Z | 2017-09-18 11:41 | 2017-09-18 12:24 | 2017-09-18 12:24 | 2017-09-19 12:58 | 25:17 | 0.98 | 1.22 | 0.24 | 7.5 | 89.6667
Note on E46: Syed Imran Ali: Seeking clarification: has aeration been removed on Side B? - Side B now no areation. We have installed additional T45 tanks on that side for in PAC dosing and then batch chlorination.
Note on E48: Syed Imran Ali: As above
Note on E50: Syed Imran Ali: This is also a storage sample correct? Yes
Note on E53: Syed Imran Ali: This one and the one below it have the same description -- but I think only sample 51 was stored overnight? Please confirm. Correct 14-8 tested that evening. 14-9 tested the following afternoon.
Note on J55: Syed Imran Ali: Same here. I've removed stored at time. No storage on this one. Straight away tested.
Note on G58: Syed Imran Ali: these timings make no sense: chlorination happened after sampling?
Note on G59: Syed Imran Ali: same as above. Also, how were they stored? Also, was the initial THM reading taken or only post storage?ding?
Note on H60: Syed Imran Ali: timing screwy here again

## A+C Data (by batch)
STAGE 1: Clarified+chlorinated at the same time | [15 empty] | STAGE 2: Post-aeration | [15 empty] | STAGE 3: Stored overnight
Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event |  |  |  |  | Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event |  |  |  |  | Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event
Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM | Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM | Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM
No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb | No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb | No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb
3 | 2017-08-23 | Sample 3 | 4A tank | Alum and chlorination at same time | B | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 0.8 | 1.11 | 0.31 |  | 95.98 | 4 | 2017-08-23 | Sample 4 | 8A inflow | Post-aeration | B | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 |  |  |  |  | 90 | [16 empty] | Post-aeration water wasted before FRC and other WQ checks done
49 | 2017-09-14 | Sept14-7 | 1A | Cl2 & Sedimentation together (Pre-aeration) | R | 2017-09-14 12:04 | 2017-09-14 16:27 | n/a | 2017-09-14 17:15 | 5:11 | 0.05 | 0.07 | 0.02 | 6.87 | 229.3333 | 50 | 2017-09-14 | Sept14-8 | 8A | Cl2 & Sedimentation together (Post-aeration) | R | 2017-09-14 12:04 | 2017-09-14 16:32 | n/a | 2017-09-14 17:15 | 5:11 | 0.8 | 1.04 | 0.24 | 7.18 | 226.3333 | 51 | 2017-09-14 | Sept14-9 | 8A | Cl2 & Sedimentation together (Post-aeration & Storage) | R | 2017-09-14 12:04 | 2017-09-14 16:32 | 2017-09-14 16:35 | 2017-09-15 16:05 | 28:01 | 0.19 | 0.27 | 0.08 | 7.07 | 249
52 | 2017-09-15 | Sept15-1 | 4A | Cl2 & Sedimentation together | S | 2017-09-15 13:19 | 2017-09-15 15:12 | n/a | 2017-09-15 15:38 | 2:19 | 0.07 | 0.56 | 0.49 | 7.27 | 282.3333 | 53 | 2017-09-15 | Sept15-2 | 4A | Inflow post aerated | S | 2017-09-15 13:19 | 2017-09-15 15:13 | n/a | 2017-09-15 15:46 | 2:27 | 0.14 | 0.57 | 0.43 | 7.18 | 266.6667
57 | 2017-09-19 | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | W | [26 empty] | 57 | 2017-09-19 | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | W | 2017-09-18 18:18 | 2017-09-18 07:03 | 2017-09-18 07:03 | 2017-09-19 12:58 | 18:40 | 0.07 | 0.27 | 0.2 | 7.2 | 204
59 | 2017-09-19 | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | Y | [26 empty] | 59 | 2017-09-19 | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | Y | 2017-09-18 11:05 | 2017-09-18 12:18 | 2017-09-18 12:18 | 2017-09-19 12:58 | 25:53 | 0.54 | 0.73 | 0.19 | 7.3 | 201
Note on U6: Syed Imran Ali: This one and the one below it have the same description -- but I think only sample 51 was stored overnight? Please confirm. Correct 14-8 tested that evening. 14-9 tested the following afternoon.
Note on J7: Syed Imran Ali: Same here. I've removed stored at time. No storage on this one. Straight away tested.
Note on AN8: Syed Imran Ali: timing screwy here again

## Pre-Clar Data (by batch)
STAGE 1: Pre-clarified then chlorinated | [15 empty] | STAGE 2: Post-aeration | [15 empty] | STAGE 3: Stored overnight
Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event |  |  |  |  | Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event |  |  |  |  | Sample Information | [5 empty] | Event Times |  |  |  |  | Water quality at THM testing event
Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM | Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM | Sample | Date | ID | Source | Description | Batch | Chlorinated at | Sampled at | Stored at | Tested at | Time elapsed | FRC | TRC | CRC | pH | THM
No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb | No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb | No. |  |  |  |  | Group |  |  |  |  | (hh:mm:ss) | (mg/L) | (mg/L) | (mg/L) |  | ppb
1 | 2017-08-23 | Sample 1 | 4B tank | Pre-clarified w/ PAC then chlorinated | A | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 1.42 | 1.65 | 0.23 |  | 60 | 2 | 2017-08-23 | Sample 2 | 7B inflow | Post-aeration | A | 2017-08-23 09:30 | 2017-08-23 10:47 | n/a | 2017-08-23 11:00 | 1:30 | 1.62 | 1.89 | 0.27 |  | 41.3333
6 | 2017-08-24 | Aug24-1 | 6B tank | Pre-clarified w/ PAC then chlorinated | C | 2017-08-24 10:02 | 2017-08-24 10:38 | n/a | 2017-08-24 10:52 | 0:50 | 1.68 | 1.9 | 0.22 |  | 46 | 7 | 2017-08-24 | Aug24-2 | 8B inflow | Post-aeration | C | 2017-08-24 10:02 | 2017-08-24 10:38 | n/a | 2017-08-24 10:52 | 0:50 | 1.77 | 1.89 | 0.12 |  | 41 | 8 | 2017-08-24 | Aug24-3 | 8B inflow | Stored overnight | C | 2017-08-24 10:02 | 2017-08-24 10:40 | 2017-08-24 10:45 | 2017-08-25 10:33 | 24:31 | 0.81 | 0.88 | 0.07 | 7.2 | 63
10 | 2017-08-24 | Aug24-5 | 4B tank | Pre-clarified w/ PAC then chlorinated | D | 2017-08-24 12:15 | 2017-08-24 12:45 | n/a | 2017-08-24 12:52 | 0:37 | 1.86 | 2 | 0.14 |  | 36 | 11 | 2017-08-24 | Aug24-6 | 9B inflow | Post-aeration | D | 2017-08-24 12:15 | 2017-08-24 12:46 | n/a | 2017-08-24 12:53 | 0:38 | 1.99 | 2.07 | 0.08 |  | 30 | 12 | 2017-08-24 | Aug24-7 | 9B inflow | Stored overnight | D | 2017-08-24 12:15 | 2017-08-24 12:49 | 2017-08-24 12:52 | 2017-08-25 10:36 | 22:21 | 0.74 | 0.83 | 0.09 | 7.27
14 | 2017-08-25 | Aug25-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | E | 2017-08-25 09:40 | 2017-08-25 10:14 | n/a | 2017-08-25 10:38 | 0:58 | 1.45 | 1.63 | 0.18 | 7.16 | 46.5 | 15 | 2017-08-25 | Aug25-2 | 7B inflow | Post-aeration | E | 2017-08-25 09:40 | 2017-08-25 10:16 | n/a | 2017-08-25 10:40 | 1:00 | 1.42 | 1.57 | 0.15 | 7.25 | 68.25 | 16 | 2017-08-25 | Aug25-3 | 7B inflow | Stored overnight | E | 2017-08-25 09:40 | 2017-08-25 10:19 | 2017-08-25 10:25 | 2017-08-26 14:26 | 28:46 | 0.68 | 0.84 | 0.16 | 0.16 | 70
17 | 2017-08-25 | Aug25-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | F | 2017-08-25 09:17 | 2017-08-25 10:21 | n/a | 2017-08-25 10:40 | 1:23 | 3.08 | 3.16 | 0.08 | 7.23 | 63.6667 | 18 | 2017-08-25 | Aug25-5 | 8B inflow | Post-aeration | F | 2017-08-25 09:17 | 2017-08-25 10:26 | n/a | 2017-08-25 10:40 | 1:23 | 3.16 | 3.27 | 0.11 | 7.28 | 56.5 | 19 | 2017-08-25 | Aug25-6 | 8B inflow | Stored overnight | F | 2017-08-25 09:17 | 2017-08-25 10:26 | 2017-08-25 10:29 | 2017-08-26 14:23 | 29:06 | 2.25 | 2.45 | 0.2 | 7.05 | 85
21 | 2017-08-26 | Aug26-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | G | 2017-08-26 13:31 | 2017-08-26 14:02 | n/a | 2017-08-26 14:14 | 0:43 | 0.91 | 1.1 | 0.19 | 6.82 | 46.5 | 22 | 2017-08-26 | Aug26-2 | 7B inflow | Post-aeration | G | 2017-08-26 13:31 | 2017-08-26 14:02 | n/a | 2017-08-26 14:15 | 0:44 | 1.16 | 1.25 | 0.09 | 6.99 | 41.75 | 23 | 2017-08-26 | Aug26-3 | 7B inflow | Stored overnight | G | 2017-08-26 13:31 | 2017-08-26 14:03 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:31 | 0.44 | 0.6 | 0.16 | 7.08 | 62.6667
24 | 2017-08-26 | Aug26-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | H | 2017-08-26 13:03 | 2017-08-26 14:02 | n/a | 2017-08-26 14:17 | 1:14 | 1.29 | 1.5 | 0.21 | 7.01 | 49 | 25 | 2017-08-26 | Aug26-5 | 8B inflow | Post-aeration | H | 2017-08-26 13:03 | 2017-08-26 14:06 | n/a | 2017-08-26 14:20 | 1:17 | 1.35 | 1.48 | 0.13 | 7.26 | 45.75 | 26 | 2017-08-26 | Aug26-6 | 8B inflow | Stored overnight | H | 2017-08-26 13:03 | 2017-08-26 14:06 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:59 | 0.71 | 0.81 | 0.1 | 7.13 | 67.8333
27 | 2017-08-27 | Aug27-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | I | 2017-08-27 12:08 | 2017-08-27 12:41 | n/a | 2017-08-27 13:08 | 1:00 | 1.35 | 1.4 | 0.05 | 7.16 | 41 | 28 | 2017-08-27 | Aug27-2 | 7B inflow | Post-aeration | I | 2017-08-27 12:08 | 2017-08-27 12:45 | n/a | 2017-08-27 13:08 | 1:00 | 1.48 | 1.69 | 0.21 | 6.77 |  | 29 | 2017-08-27 | Aug27-3 | 7B inflow | Stored overnight | I | 2017-08-27 12:08 | 2017-08-27 12:43 | 2017-08-27 12:50 | 2017-08-28 16:27 | 28:19 | 0.57 | 0.74 | 0.17 | 7.17 | 63.3333
30 | 2017-08-27 | Aug27-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | J | 2017-08-27 12:10 | 2017-08-27 12:46 | n/a | 2017-08-27 13:08 | 0:58 | 1.79 | 1.86 | 0.07 | 7.24 | 52.6667 | 31 | 2017-08-27 | Aug27-5 | 8B inflow | Post-aeration | J | 2017-08-27 12:10 | 2017-08-27 12:46 | n/a | 2017-08-27 13:08 | 0:58 | 1.67 | 1.8 | 0.13 | 7.33 | 54 | 32 | 2017-08-27 | Aug27-6 | 8B inflow | Stored overnight | J | 2017-08-27 12:10 | 2017-08-27 12:46 | 2017-08-27 12:50 | 2017-08-28 16:24 | 28:14 | 0.93 | 1.27 | 0.34 | 7.31 | 75.3333
33 | 2017-08-28 | Aug28-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | K | 2017-08-28 15:03 | 2017-08-28 15:53 | n/a | 2017-08-28 16:11 | 1:08 | 1.1 | 1.33 | 0.23 | 7.11 | 50.3333 | 34 | 2017-08-28 | Aug28-2 | 7B inflow | Post-aeration | K | 2017-08-28 15:03 | 2017-08-28 15:55 | n/a | 2017-08-28 16:13 | 1:10 | 1.23 | 1.36 | 0.13 | 7.21 | 46 | 35 | 2017-08-28 | Aug28-3 | 7B inflow | Stored overnight | K | 2017-08-28 15:03 | 2017-08-28 15:58 | 2017-08-28 16:08 | 2017-08-29 10:37 | 19:34 | 0.37 | 0.53 | 0.16 | 7.35 | 59.3333
36 | 2017-08-28 | Aug28-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | L | 2017-08-28 14:21 | 2017-08-28 16:01 | n/a | 2017-08-28 16:22 | 2:01 | 2.58 | 2.71 | 0.13 | 7.13 | 60.3333 | 37 | 2017-08-28 | Aug28-5 | 8B inflow | Post-aeration | L | 2017-08-28 14:21 | 2017-08-28 16:05 | n/a | 2017-08-28 16:22 | 2:01 | 2.83 | 2.91 | 0.08 | 7.17 | 45 | 38 | 2017-08-28 | Aug28-6 | 8B inflow | Stored overnight | L | 2017-08-28 14:21 | 2017-08-28 16:04 | 2017-08-28 16:08 | 2017-08-29 10:38 | 20:17 | 1.65 | 1.8 | 0.15 | 7.37 | 44.6667
39 | 2017-08-29 | Aug29-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | M | 2017-08-29 08:10 | 2017-08-29 10:19 | n/a | 2017-08-29 10:29 | 2:19 | 4.09 | 4.26 | 0.17 | 7.01 | 55.3333 | 40 | 2017-08-29 | Aug29-2 | 7B inflow | Post-aeration | M | 2017-08-29 08:10 | 2017-08-29 10:25 | n/a | 2017-08-29 10:29 | 2:19 | 4.02 | 4.16 | 0.14 | 7.06 | 51.6667
41 | 2017-08-29 | Aug29-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | N | 2017-08-29 08:05 | 2017-08-29 10:12 | n/a | 2017-08-29 10:33 | 2:28 | 1.58 | 1.73 | 0.15 | 7.16 | 48.6667 | 42 | 2017-08-29 | Aug29-5 | 8B inflow | Post-aeration | N | 2017-08-29 08:05 | 2017-08-29 10:16 | n/a | 2017-08-29 10:34 | 2:29 | 1.34 | 1.63 | 0.29 | 7.18 | 54.3333
44 | 2017-09-14 | Sept14-2 | 8B | Batch Cl2 post sedimentation | O | 2017-09-14 14:29 | 2017-09-14 16:09 | n/a | 2017-09-14 17:15 | 2:46 | 1.43 | 1.52 | 0.09 | 7.16 | 83.6667 | [16 empty] | 43 | 2017-09-14 | Sept14-1 | 8B | Batch Cl2 post sedimentation + Storage | O | 2017-09-14 14:19 | 2017-09-14 16:08 | 2017-09-14 16:35 | 2017-09-15 16:05 | 25:46 | 0.23 | 0.34 | 0.11 | 7.09 | 117.3333
46 | 2017-09-14 | Sept14-4 | 7B | Batch Cl2 post sedimentation | P | 2017-09-14 13:27 | 2017-09-14 16:14 | n/a | 2017-09-14 17:15 | 3:48 | 1.58 | 1.69 | 0.11 | 7.28 | 89.3333 | [16 empty] | 45 | 2017-09-14 | Sept14-3 | 7B | Batch Cl2 post sedimentation + Storage | P | 2017-09-14 13:27 | 2017-09-14 16:13 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:38 | 0.55 | 0.62 | 0.07 | 6.67 | 129
48 | 2017-09-14 | Sept14-6 | 9A | Batch Cl2 post sedimentation | Q | 2017-09-14 13:36 | 2017-09-14 16:21 | n/a | 2017-09-14 17:15 | 3:39 | 1.93 | 2.18 | 0.25 | 6.86 | 89 | [16 empty] | 47 | 2017-09-14 | Sept14-5 | 9A | Batch Cl2 post sedimentation + Storage | Q | 2017-09-14 13:36 | 2017-09-14 16:21 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:29 | 0.48 | 0.62 | 0.14 | 7.09 | 133.6667
54 | 2017-09-15 | Sept15-3 | 8B | Batch Cl2 post sedimentation | T | 2017-09-15 12:22 | 2017-09-15 15:18 | n/a | 2017-09-15 15:23 | 3:01 | 0.65 | 0.8 | 0.15 | 7.31 | 91
55 | 2017-09-19 | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight | U | [26 empty] | 55 | 2017-09-19 | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight | U | 2017-09-18 17:02 |  |  | 2017-09-19 12:58 | 19:56 | 0.06 | 0.27 | 0.21 | 7.1 | 99 | Unclear on timings and method of storage (in sealed bottle, or tank over night)
56 | 2017-09-19 | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight | V | [26 empty] | 56 | 2017-09-19 | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight | V | 2017-09-18 18:41 |  |  | 2017-09-19 12:58 | 18:17 | 0.4 | 0.72 | 0.32 | 6.9 | 107.3333 | Unclear on timings and method of storage (in sealed bottle, or tank over night)
58 | 2017-09-19 | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | X | [26 empty] | 58 | 2017-09-19 | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | X | 2017-09-18 10:00 | 2017-09-18 12:16 | 2017-09-18 12:16 | 2017-09-19 12:58 | 26:58 | 0.74 | 0.9 | 0.16 | 7.5 | 93 | Unclear on method of storage (sealed bottle or in tank overnight)
60 | 2017-09-19 | Sept19-06 | 9A | Batch Cl2 post sedimentation. | Z | [26 empty] | 60 | 2017-09-19 | Sept19-06 | 9A | Batch Cl2 post sedimentation. | Z | 2017-09-18 11:41 | 2017-09-18 12:24 | 2017-09-18 12:24 | 2017-09-19 12:58 | 25:17 | 0.98 | 1.22 | 0.24 | 7.5 | 89.6667 | Unclear on method of storage (sealed bottle or in tank overnight)

## STATA import (Pre-clar)
batch_no | date_started | id_s1 | source_s1 | desc_s1 | chlorinated_time | sampled_time_s1 | tested_time_s1 | time_elapsed_s1 | frc_s1 | trc_s1 | crc_s1 | ph_s1 | thm_s1 | id_s2 | source_s2 | desc_s2 | sampled_time_s2 | tested_time_s2 | time_elapsed_s2 | frc_s2 | trc_s2 | crc_s2 | ph_s2 | thm_s2 | id_s3 | source_s3 | desc_s3 | sampled_time_s3 | stored_time_s3 | tested_time_s3 | time_elapsed_s3 | frc_s3 | trc_s3 | crc_s3 | ph_s3 | thm_s3 | run | side
1 | 2017-08-23 | Sample 1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-23 09:30 | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 1.42 | 1.65 | 0.23 |  | 60 | Sample 2 | 7B inflow | Post-aeration | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 1.62 | 1.89 | 0.27 |  | 41.3333 | [12 empty] | 1 | 1
2 | 2017-08-24 | Aug24-1 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-24 10:02 | 2017-08-24 10:38 | 2017-08-24 10:52 | 0:50 | 1.68 | 1.9 | 0.22 |  | 46 | Aug24-2 | 8B inflow | Post-aeration | 2017-08-24 10:38 | 2017-08-24 10:52 | 0:50 | 1.77 | 1.89 | 0.12 |  | 41 | Aug24-3 | 8B inflow | Stored overnight | 2017-08-24 10:40 | 2017-08-24 10:45 | 2017-08-25 10:33 | 24:31 | 0.81 | 0.88 | 0.07 | 7.2 | 63 | 1 | 1
3 | 2017-08-24 | Aug24-5 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-24 12:15 | 2017-08-24 12:45 | 2017-08-24 12:52 | 0:37 | 1.86 | 2 | 0.14 |  | 36 | Aug24-6 | 9B inflow | Post-aeration | 2017-08-24 12:46 | 2017-08-24 12:53 | 0:38 | 1.99 | 2.07 | 0.08 |  | 30 | Aug24-7 | 9B inflow | Stored overnight | 2017-08-24 12:49 | 2017-08-24 12:52 | 2017-08-25 10:36 | 22:21 | 0.74 | 0.83 | 0.09 | 7.27 |  | 1 | 1
4 | 2017-08-25 | Aug25-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-25 09:40 | 2017-08-25 10:14 | 2017-08-25 10:38 | 0:58 | 1.45 | 1.63 | 0.18 | 7.16 | 46.5 | Aug25-2 | 7B inflow | Post-aeration | 2017-08-25 10:16 | 2017-08-25 10:40 | 1:00 | 1.42 | 1.57 | 0.15 | 7.25 | 68.25 | Aug25-3 | 7B inflow | Stored overnight | 2017-08-25 10:19 | 2017-08-25 10:25 | 2017-08-26 14:26 | 28:46 | 0.68 | 0.84 | 0.16 | 0.16 | 70 | 1 | 1
5 | 2017-08-25 | Aug25-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-25 09:17 | 2017-08-25 10:21 | 2017-08-25 10:40 | 1:23 | 3.08 | 3.16 | 0.08 | 7.23 | 63.6667 | Aug25-5 | 8B inflow | Post-aeration | 2017-08-25 10:26 | 2017-08-25 10:40 | 1:23 | 3.16 | 3.27 | 0.11 | 7.28 | 56.5 | Aug25-6 | 8B inflow | Stored overnight | 2017-08-25 10:26 | 2017-08-25 10:29 | 2017-08-26 14:23 | 29:06 | 2.25 | 2.45 | 0.2 | 7.05 | 85 | 1 | 1
6 | 2017-08-26 | Aug26-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-26 13:31 | 2017-08-26 14:02 | 2017-08-26 14:14 | 0:43 | 0.91 | 1.1 | 0.19 | 6.82 | 46.5 | Aug26-2 | 7B inflow | Post-aeration | 2017-08-26 14:02 | 2017-08-26 14:15 | 0:44 | 1.16 | 1.25 | 0.09 | 6.99 | 41.75 | Aug26-3 | 7B inflow | Stored overnight | 2017-08-26 14:03 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:31 | 0.44 | 0.6 | 0.16 | 7.08 | 62.6667 | 1 | 1
7 | 2017-08-26 | Aug26-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-26 13:03 | 2017-08-26 14:02 | 2017-08-26 14:17 | 1:14 | 1.29 | 1.5 | 0.21 | 7.01 | 49 | Aug26-5 | 8B inflow | Post-aeration | 2017-08-26 14:06 | 2017-08-26 14:20 | 1:17 | 1.35 | 1.48 | 0.13 | 7.26 | 45.75 | Aug26-6 | 8B inflow | Stored overnight | 2017-08-26 14:06 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:59 | 0.71 | 0.81 | 0.1 | 7.13 | 67.8333 | 1 | 1
8 | 2017-08-27 | Aug27-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-27 12:08 | 2017-08-27 12:41 | 2017-08-27 13:08 | 1:00 | 1.35 | 1.4 | 0.05 | 7.16 | 41 | Aug27-2 | 7B inflow | Post-aeration | 2017-08-27 12:45 | 2017-08-27 13:08 | 1:00 | 1.48 | 1.69 | 0.21 | 6.77 |  | Aug27-3 | 7B inflow | Stored overnight | 2017-08-27 12:43 | 2017-08-27 12:50 | 2017-08-28 16:27 | 28:19 | 0.57 | 0.74 | 0.17 | 7.17 | 63.3333 | 1 | 1
9 | 2017-08-27 | Aug27-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-27 12:10 | 2017-08-27 12:46 | 2017-08-27 13:08 | 0:58 | 1.79 | 1.86 | 0.07 | 7.24 | 52.6667 | Aug27-5 | 8B inflow | Post-aeration | 2017-08-27 12:46 | 2017-08-27 13:08 | 0:58 | 1.67 | 1.8 | 0.13 | 7.33 | 54 | Aug27-6 | 8B inflow | Stored overnight | 2017-08-27 12:46 | 2017-08-27 12:50 | 2017-08-28 16:24 | 28:14 | 0.93 | 1.27 | 0.34 | 7.31 | 75.3333 | 1 | 1
10 | 2017-08-28 | Aug28-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-28 15:03 | 2017-08-28 15:53 | 2017-08-28 16:11 | 1:08 | 1.1 | 1.33 | 0.23 | 7.11 | 50.3333 | Aug28-2 | 7B inflow | Post-aeration | 2017-08-28 15:55 | 2017-08-28 16:13 | 1:10 | 1.23 | 1.36 | 0.13 | 7.21 | 46 | Aug28-3 | 7B inflow | Stored overnight | 2017-08-28 15:58 | 2017-08-28 16:08 | 2017-08-29 10:37 | 19:34 | 0.37 | 0.53 | 0.16 | 7.35 | 59.3333 | 1 | 1
11 | 2017-08-28 | Aug28-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-28 14:21 | 2017-08-28 16:01 | 2017-08-28 16:22 | 2:01 | 2.58 | 2.71 | 0.13 | 7.13 | 60.3333 | Aug28-5 | 8B inflow | Post-aeration | 2017-08-28 16:05 | 2017-08-28 16:22 | 2:01 | 2.83 | 2.91 | 0.08 | 7.17 | 45 | Aug28-6 | 8B inflow | Stored overnight | 2017-08-28 16:04 | 2017-08-28 16:08 | 2017-08-29 10:38 | 20:17 | 1.65 | 1.8 | 0.15 | 7.37 | 44.6667 | 1 | 1
12 | 2017-08-29 | Aug29-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-29 08:10 | 2017-08-29 10:19 | 2017-08-29 10:29 | 2:19 | 4.09 | 4.26 | 0.17 | 7.01 | 55.3333 | Aug29-2 | 7B inflow | Post-aeration | 2017-08-29 10:25 | 2017-08-29 10:29 | 2:19 | 4.02 | 4.16 | 0.14 | 7.06 | 51.6667 | [12 empty] | 1 | 1
13 | 2017-08-29 | Aug29-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-29 08:05 | 2017-08-29 10:12 | 2017-08-29 10:33 | 2:28 | 1.58 | 1.73 | 0.15 | 7.16 | 48.6667 | Aug29-5 | 8B inflow | Post-aeration | 2017-08-29 10:16 | 2017-08-29 10:34 | 2:29 | 1.34 | 1.63 | 0.29 | 7.18 | 54.3333 | [12 empty] | 1 | 1
14 | 2017-09-14 | Sept14-2 | 8B | Batch Cl2 post sedimentation | 2017-09-14 14:29 | 2017-09-14 16:09 | 2017-09-14 17:15 | 2:46 | 1.43 | 1.52 | 0.09 | 7.16 | 83.6667 | [11 empty] | Sept14-1 | 8B | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:08 | 2017-09-14 16:35 | 2017-09-15 16:05 | 25:36 | 0.23 | 0.34 | 0.11 | 7.09 | 117.3333 | 2 | 1
15 | 2017-09-14 | Sept14-4 | 7B | Batch Cl2 post sedimentation | 2017-09-14 13:27 | 2017-09-14 16:14 | 2017-09-14 17:15 | 3:48 | 1.58 | 1.69 | 0.11 | 7.28 | 89.3333 | [11 empty] | Sept14-3 | 7B | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:13 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:38 | 0.55 | 0.62 | 0.07 | 6.67 | 129 | 2 | 1
16 | 2017-09-14 | Sept14-6 | 9A | Batch Cl2 post sedimentation | 2017-09-14 13:36 | 2017-09-14 16:21 | 2017-09-14 17:15 | 3:39 | 1.93 | 2.18 | 0.25 | 6.86 | 89 | [11 empty] | Sept14-5 | 9A | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:21 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:29 | 0.48 | 0.62 | 0.14 | 7.09 | 133.6667 | 2 | 1
17 | 2017-09-15 | Sept15-3 | 8B | Batch Cl2 post sedimentation | 2017-09-15 12:22 | 2017-09-15 15:18 | 2017-09-15 15:23 | 3:01 | 0.65 | 0.8 | 0.15 | 7.31 | 91 | [23 empty] | 2 | 1
18 | 2017-09-19 | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight | [20 empty] | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight |  |  | 2017-09-19 12:58 |  | 0.06 | 0.27 | 0.21 | 7.1 | 99 | 2 | 1
19 | 2017-09-19 | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight | [20 empty] | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight |  |  | 2017-09-19 12:58 |  | 0.4 | 0.72 | 0.32 | 6.9 | 107.3333 | 2 | 1
20 | 2017-09-19 | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | [20 empty] | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | 2017-09-18 12:16 | 2017-09-18 12:16 | 2017-09-19 12:58 |  | 0.74 | 0.9 | 0.16 | 7.5 | 93 | 2 | 1
21 | 2017-09-19 | Sept19-06 | 9A | Batch Cl2 post sedimentation. | [20 empty] | Sept19-06 | 9A | Batch Cl2 post sedimentation. | 2017-09-18 12:24 | 2017-09-18 12:24 | 2017-09-19 12:58 |  | 0.98 | 1.22 | 0.24 | 7.5 | 89.6667 | 2 | 1

## STATA import (A+C)
batch_no | date_started | id_s1 | source_s1 | desc_s1 | chlorinated_time | sampled_time_s1 | tested_time_s1 | time_elapsed_s1 | frc_s1 | trc_s1 | crc_s1 | ph_s1 | thm_s1 | id_s2 | source_s2 | desc_s2 | sampled_time_s2 | tested_time_s2 | time_elapsed_s2 | frc_s2 | trc_s2 | crc_s2 | ph_s2 | thm_s2 | id_s3 | source_s3 | desc_s3 | sampled_time_s3 | stored_time_s3 | tested_time_s3 | time_elapsed_s3 | frc_s3 | trc_s3 | crc_s3 | ph_s3 | thm_s3 | run | side
22 | 2017-08-23 | Sample 3 | 4A tank | Alum and chlorination at same time | 2017-08-23 09:30 | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 0.8 | 1.11 | 0.31 |  | 95.98 | Sample 4 | 8A inflow | Post-aeration | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 |  |  |  |  | 90 | [12 empty] | 1 | 2
23 | 2017-09-14 | Sept14-7 | 1A | Cl2 & Sedimentation together (Pre-aeration) | 2017-09-14 12:04 | 2017-09-14 16:27 | 2017-09-14 17:15 | 5:11 | 0.05 | 0.07 | 0.02 | 6.87 | 229.3333 | Sept14-8 | 8A | Cl2 & Sedimentation together (Post-aeration) | 2017-09-14 16:32 | 2017-09-14 17:15 | 5:11 | 0.8 | 1.04 | 0.24 | 7.18 | 226.3333 | Sept14-9 | 8A | Cl2 & Sedimentation together (Post-aeration & Storage) | 2017-09-14 16:32 | 2017-09-14 16:35 | 2017-09-15 16:05 | 28:01 | 0.19 | 0.27 | 0.08 | 7.07 | 249 | 2 | 2
24 | 2017-09-15 | Sept15-1 | 4A | Cl2 & Sedimentation together | 2017-09-15 13:19 | 2017-09-15 15:12 | 2017-09-15 15:38 | 2:19 | 0.07 | 0.56 | 0.49 | 7.27 | 282.3333 | Sept15-2 | 4A | Inflow post aerated | 2017-09-15 15:13 | 2017-09-15 15:46 | 2:27 | 0.14 | 0.57 | 0.43 | 7.18 | 266.6667 | [12 empty] | 2 | 2
25 | 2017-09-19 | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | [20 empty] | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | 2017-09-18 07:03 | 2017-09-18 07:03 | 2017-09-19 12:58 |  | 0.07 | 0.27 | 0.2 | 7.2 | 204 | 2 | 2
26 | 2017-09-19 | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | [20 empty] | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | 2017-09-18 12:18 | 2017-09-18 12:18 | 2017-09-19 12:58 |  | 0.54 | 0.73 | 0.19 | 7.3 | 201 | 2 | 2

## STATA import (all)
batch_no | date_started | id_s1 | source_s1 | desc_s1 | chlorinated_time | sampled_time_s1 | tested_time_s1 | time_elapsed_s1 | frc_s1 | trc_s1 | crc_s1 | ph_s1 | thm_s1 | id_s2 | source_s2 | desc_s2 | sampled_time_s2 | tested_time_s2 | time_elapsed_s2 | frc_s2 | trc_s2 | crc_s2 | ph_s2 | thm_s2 | id_s3 | source_s3 | desc_s3 | sampled_time_s3 | stored_time_s3 | tested_time_s3 | time_elapsed_s3 | frc_s3 | trc_s3 | crc_s3 | ph_s3 | thm_s3 | run | side
1 | 2017-08-23 | Sample 1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-23 09:30 | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 1.42 | 1.65 | 0.23 |  | 60 | Sample 2 | 7B inflow | Post-aeration | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 1.62 | 1.89 | 0.27 |  | 41.3333 | [12 empty] | 1 | 1
2 | 2017-08-24 | Aug24-1 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-24 10:02 | 2017-08-24 10:38 | 2017-08-24 10:52 | 0:50 | 1.68 | 1.9 | 0.22 |  | 46 | Aug24-2 | 8B inflow | Post-aeration | 2017-08-24 10:38 | 2017-08-24 10:52 | 0:50 | 1.77 | 1.89 | 0.12 |  | 41 | Aug24-3 | 8B inflow | Stored overnight | 2017-08-24 10:40 | 2017-08-24 10:45 | 2017-08-25 10:33 | 24:31 | 0.81 | 0.88 | 0.07 | 7.2 | 63 | 1 | 1
3 | 2017-08-24 | Aug24-5 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-24 12:15 | 2017-08-24 12:45 | 2017-08-24 12:52 | 0:37 | 1.86 | 2 | 0.14 |  | 36 | Aug24-6 | 9B inflow | Post-aeration | 2017-08-24 12:46 | 2017-08-24 12:53 | 0:38 | 1.99 | 2.07 | 0.08 |  | 30 | Aug24-7 | 9B inflow | Stored overnight | 2017-08-24 12:49 | 2017-08-24 12:52 | 2017-08-25 10:36 | 22:21 | 0.74 | 0.83 | 0.09 | 7.27 |  | 1 | 1
4 | 2017-08-25 | Aug25-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-25 09:40 | 2017-08-25 10:14 | 2017-08-25 10:38 | 0:58 | 1.45 | 1.63 | 0.18 | 7.16 | 46.5 | Aug25-2 | 7B inflow | Post-aeration | 2017-08-25 10:16 | 2017-08-25 10:40 | 1:00 | 1.42 | 1.57 | 0.15 | 7.25 | 68.25 | Aug25-3 | 7B inflow | Stored overnight | 2017-08-25 10:19 | 2017-08-25 10:25 | 2017-08-26 14:26 | 28:46 | 0.68 | 0.84 | 0.16 | 0.16 | 70 | 1 | 1
5 | 2017-08-25 | Aug25-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-25 09:17 | 2017-08-25 10:21 | 2017-08-25 10:40 | 1:23 | 3.08 | 3.16 | 0.08 | 7.23 | 63.6667 | Aug25-5 | 8B inflow | Post-aeration | 2017-08-25 10:26 | 2017-08-25 10:40 | 1:23 | 3.16 | 3.27 | 0.11 | 7.28 | 56.5 | Aug25-6 | 8B inflow | Stored overnight | 2017-08-25 10:26 | 2017-08-25 10:29 | 2017-08-26 14:23 | 29:06 | 2.25 | 2.45 | 0.2 | 7.05 | 85 | 1 | 1
6 | 2017-08-26 | Aug26-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-26 13:31 | 2017-08-26 14:02 | 2017-08-26 14:14 | 0:43 | 0.91 | 1.1 | 0.19 | 6.82 | 46.5 | Aug26-2 | 7B inflow | Post-aeration | 2017-08-26 14:02 | 2017-08-26 14:15 | 0:44 | 1.16 | 1.25 | 0.09 | 6.99 | 41.75 | Aug26-3 | 7B inflow | Stored overnight | 2017-08-26 14:03 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:31 | 0.44 | 0.6 | 0.16 | 7.08 | 62.6667 | 1 | 1
7 | 2017-08-26 | Aug26-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-26 13:03 | 2017-08-26 14:02 | 2017-08-26 14:17 | 1:14 | 1.29 | 1.5 | 0.21 | 7.01 | 49 | Aug26-5 | 8B inflow | Post-aeration | 2017-08-26 14:06 | 2017-08-26 14:20 | 1:17 | 1.35 | 1.48 | 0.13 | 7.26 | 45.75 | Aug26-6 | 8B inflow | Stored overnight | 2017-08-26 14:06 | 2017-08-26 14:08 | 2017-08-27 13:02 | 23:59 | 0.71 | 0.81 | 0.1 | 7.13 | 67.8333 | 1 | 1
8 | 2017-08-27 | Aug27-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-27 12:08 | 2017-08-27 12:41 | 2017-08-27 13:08 | 1:00 | 1.35 | 1.4 | 0.05 | 7.16 | 41 | Aug27-2 | 7B inflow | Post-aeration | 2017-08-27 12:45 | 2017-08-27 13:08 | 1:00 | 1.48 | 1.69 | 0.21 | 6.77 |  | Aug27-3 | 7B inflow | Stored overnight | 2017-08-27 12:43 | 2017-08-27 12:50 | 2017-08-28 16:27 | 28:19 | 0.57 | 0.74 | 0.17 | 7.17 | 63.3333 | 1 | 1
9 | 2017-08-27 | Aug27-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-27 12:10 | 2017-08-27 12:46 | 2017-08-27 13:08 | 0:58 | 1.79 | 1.86 | 0.07 | 7.24 | 52.6667 | Aug27-5 | 8B inflow | Post-aeration | 2017-08-27 12:46 | 2017-08-27 13:08 | 0:58 | 1.67 | 1.8 | 0.13 | 7.33 | 54 | Aug27-6 | 8B inflow | Stored overnight | 2017-08-27 12:46 | 2017-08-27 12:50 | 2017-08-28 16:24 | 28:14 | 0.93 | 1.27 | 0.34 | 7.31 | 75.3333 | 1 | 1
10 | 2017-08-28 | Aug28-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-28 15:03 | 2017-08-28 15:53 | 2017-08-28 16:11 | 1:08 | 1.1 | 1.33 | 0.23 | 7.11 | 50.3333 | Aug28-2 | 7B inflow | Post-aeration | 2017-08-28 15:55 | 2017-08-28 16:13 | 1:10 | 1.23 | 1.36 | 0.13 | 7.21 | 46 | Aug28-3 | 7B inflow | Stored overnight | 2017-08-28 15:58 | 2017-08-28 16:08 | 2017-08-29 10:37 | 19:34 | 0.37 | 0.53 | 0.16 | 7.35 | 59.3333 | 1 | 1
11 | 2017-08-28 | Aug28-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-28 14:21 | 2017-08-28 16:01 | 2017-08-28 16:22 | 2:01 | 2.58 | 2.71 | 0.13 | 7.13 | 60.3333 | Aug28-5 | 8B inflow | Post-aeration | 2017-08-28 16:05 | 2017-08-28 16:22 | 2:01 | 2.83 | 2.91 | 0.08 | 7.17 | 45 | Aug28-6 | 8B inflow | Stored overnight | 2017-08-28 16:04 | 2017-08-28 16:08 | 2017-08-29 10:38 | 20:17 | 1.65 | 1.8 | 0.15 | 7.37 | 44.6667 | 1 | 1
12 | 2017-08-29 | Aug29-1 | 4B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-29 08:10 | 2017-08-29 10:19 | 2017-08-29 10:29 | 2:19 | 4.09 | 4.26 | 0.17 | 7.01 | 55.3333 | Aug29-2 | 7B inflow | Post-aeration | 2017-08-29 10:25 | 2017-08-29 10:29 | 2:19 | 4.02 | 4.16 | 0.14 | 7.06 | 51.6667 | [12 empty] | 1 | 1
13 | 2017-08-29 | Aug29-4 | 6B tank | Pre-clarified w/ PAC then chlorinated | 2017-08-29 08:05 | 2017-08-29 10:12 | 2017-08-29 10:33 | 2:28 | 1.58 | 1.73 | 0.15 | 7.16 | 48.6667 | Aug29-5 | 8B inflow | Post-aeration | 2017-08-29 10:16 | 2017-08-29 10:34 | 2:29 | 1.34 | 1.63 | 0.29 | 7.18 | 54.3333 | [12 empty] | 1 | 1
14 | 2017-09-14 | Sept14-2 | 8B | Batch Cl2 post sedimentation | 2017-09-14 14:29 | 2017-09-14 16:09 | 2017-09-14 17:15 | 2:46 | 1.43 | 1.52 | 0.09 | 7.16 | 83.6667 | [11 empty] | Sept14-1 | 8B | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:08 | 2017-09-14 16:35 | 2017-09-15 16:05 | 25:36 | 0.23 | 0.34 | 0.11 | 7.09 | 117.3333 | 2 | 1
15 | 2017-09-14 | Sept14-4 | 7B | Batch Cl2 post sedimentation | 2017-09-14 13:27 | 2017-09-14 16:14 | 2017-09-14 17:15 | 3:48 | 1.58 | 1.69 | 0.11 | 7.28 | 89.3333 | [11 empty] | Sept14-3 | 7B | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:13 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:38 | 0.55 | 0.62 | 0.07 | 6.67 | 129 | 2 | 1
16 | 2017-09-14 | Sept14-6 | 9A | Batch Cl2 post sedimentation | 2017-09-14 13:36 | 2017-09-14 16:21 | 2017-09-14 17:15 | 3:39 | 1.93 | 2.18 | 0.25 | 6.86 | 89 | [11 empty] | Sept14-5 | 9A | Batch Cl2 post sedimentation + Storage | 2017-09-14 16:21 | 2017-09-14 16:35 | 2017-09-15 16:05 | 26:29 | 0.48 | 0.62 | 0.14 | 7.09 | 133.6667 | 2 | 1
17 | 2017-09-15 | Sept15-3 | 8B | Batch Cl2 post sedimentation | 2017-09-15 12:22 | 2017-09-15 15:18 | 2017-09-15 15:23 | 3:01 | 0.65 | 0.8 | 0.15 | 7.31 | 91 | [23 empty] | 2 | 1
18 | 2017-09-19 | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight | [20 empty] | Sept19-01 | 7B | Post Sedimentation & Chlorination into 7B. Then Stayed overnight |  |  | 2017-09-19 12:58 |  | 0.06 | 0.27 | 0.21 | 7.1 | 99 | 2 | 1
19 | 2017-09-19 | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight | [20 empty] | Sept19-02 | 9A | Post Sedimentation & Chlorination into 9A. Then Stayed overnight |  |  | 2017-09-19 12:58 |  | 0.4 | 0.72 | 0.32 | 6.9 | 107.3333 | 2 | 1
20 | 2017-09-19 | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | [20 empty] | Sept19-04 | 7B | Batch Cl2 post sedimentation from 1B | 2017-09-18 12:16 | 2017-09-18 12:16 | 2017-09-19 12:58 |  | 0.74 | 0.9 | 0.16 | 7.5 | 93 | 2 | 1
21 | 2017-09-19 | Sept19-06 | 9A | Batch Cl2 post sedimentation. | [20 empty] | Sept19-06 | 9A | Batch Cl2 post sedimentation. | 2017-09-18 12:24 | 2017-09-18 12:24 | 2017-09-19 12:58 |  | 0.98 | 1.22 | 0.24 | 7.5 | 89.6667 | 2 | 1
22 | 2017-08-23 | Sample 3 | 4A tank | Alum and chlorination at same time | 2017-08-23 09:30 | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 | 0.8 | 1.11 | 0.31 |  | 95.98 | Sample 4 | 8A inflow | Post-aeration | 2017-08-23 10:47 | 2017-08-23 11:00 | 1:30 |  |  |  |  | 90 | [12 empty] | 1 | 2
23 | 2017-09-14 | Sept14-7 | 1A | Cl2 & Sedimentation together (Pre-aeration) | 2017-09-14 12:04 | 2017-09-14 16:27 | 2017-09-14 17:15 | 5:11 | 0.05 | 0.07 | 0.02 | 6.87 | 229.3333 | Sept14-8 | 8A | Cl2 & Sedimentation together (Post-aeration) | 2017-09-14 16:32 | 2017-09-14 17:15 | 5:11 | 0.8 | 1.04 | 0.24 | 7.18 | 226.3333 | Sept14-9 | 8A | Cl2 & Sedimentation together (Post-aeration & Storage) | 2017-09-14 16:32 | 2017-09-14 16:35 | 2017-09-15 16:05 | 28:01 | 0.19 | 0.27 | 0.08 | 7.07 | 249 | 2 | 2
24 | 2017-09-15 | Sept15-1 | 4A | Cl2 & Sedimentation together | 2017-09-15 13:19 | 2017-09-15 15:12 | 2017-09-15 15:38 | 2:19 | 0.07 | 0.56 | 0.49 | 7.27 | 282.3333 | Sept15-2 | 4A | Inflow post aerated | 2017-09-15 15:13 | 2017-09-15 15:46 | 2:27 | 0.14 | 0.57 | 0.43 | 7.18 | 266.6667 | [12 empty] | 2 | 2
25 | 2017-09-19 | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | [20 empty] | Sept19-03 | 8A | Cl2 & Sedimentation together. Post aeration sample over night into 8A | 2017-09-18 07:03 | 2017-09-18 07:03 | 2017-09-19 12:58 |  | 0.07 | 0.27 | 0.2 | 7.2 | 204 | 2 | 2
26 | 2017-09-19 | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | [20 empty] | Sept19-05 | 8A | Cl2 & Sedimentation together. Post aeration sample. | 2017-09-18 12:18 | 2017-09-18 12:18 | 2017-09-19 12:58 |  | 0.54 | 0.73 | 0.19 | 7.3 | 201 | 2 | 2

## Raw Water Data
Jar
| 1 | 2 | 3 | 4
Volume (L) | 10 | 10 | 10 | 10
Turbidity (NTU) | 9.9 | 9.9 | 9.9 | 9.9
1% Sol'n Dose (ml) | 2 | 3.5 | 5 | 7
Reaction time (min) | 30 | 30 | 30 | 30
FRC (mg/L) | 0.33 | 1.39 | 2.27 | 4.02
TRC (mg/L) | 0.54 | 1.76 | 2.58 | 4.16
CRC (mg/L) | 0.21 | 0.37 | 0.31 | 0.14
THM (ppb) | 106 | 117 | 131 | 151
THM increases (linearly almost) with increasing Cl dose --->
Note: Current direct chlorination dose (Al+Cl on Side A) is 10.5 L of 1% solution in 30,000 L tank. This is equivalent to 3.5 ml 1% solution in 10 L, which this jar test centres around.

## Form
Palorinya SWTP THM Study - Data Form
Date: | ____________________________
Lab Tech Names: | ____________________________
Sample No.
Sample ID
Source
Description
Batch Group
Chlorinated at:
Sampled at:
Stored at:
Tested at:
FRC (mg/L)
TRC (mg/L)
pH
THM (ppb)
Comments