## List1
Assessment of heat pump technology |  |  |  |  | Auxiliary calculations - do not delete
Input data for calculation
Eq. 7
Symbol | Variable | Unit | Value
k | Hydraulic conductivity | m/s | 0.00125
i | Groundwater gradient | m/m | 0.001 | [6 empty] | Eq. 8
n | Porosity | --- | 0.3
b | Thickness of aquifer | m | 10
L | Distance of wells | m | 50 |  |  | Y | 66.8428 | m
Q | Pumped amount of water | m3/s | 0.008 |  |  | Qback | 0.0045061 | m3/s
- values marked in yellow are to be filled out
Auxiliary quantities
STEP 1 | [5 empty] | R | 3 | ---
Evaluation of the hydraulic separation of wells | [5 empty] | t | 15811200 | s | 183 days (1/2 year)
If the wells are hydraulically separated, there is no increase in temperature in the pumped well due to the inflow of already heated water. For this, the condition must be met
Eq. 4
2Q/Tπi | 407.4367 | m
L | 50 | m |  |  |  | condition of hydraulic separation of wells
Is the condition met?
No, proceed to step 2
Is the condition met?
STEP 2
Determination of the time of temperature backflow
If the wells are not hydraulically separated, the resulting system can still be used until the thermally adjusted water flows back into the pumped well.
Eq. 9
[6 empty] | β | 8.1487
the time when a temperature change will manifest in the pumped well
tthe | 37.8303 | day |  | Eq. 12
Water flow time
number of days of the heating/cooling season | [9 empty] | Eq. 10
| 180 | day
| - if not specified less - half a year (183 days) |  |  |  |  | thyd | 12.6101 | day
Is the given period covered?
| No | - proceed to step 3 |  |  |  | Heat transport time
Eq. 13
STEP 3
Determination of the thermal cloud range
Determination of the estimated dimensions of the thermal cloud that will spread into the surroundings according to figure. The length of the cloud is marked Xcloud and the width of the cloud is marked Ycloud. The parameters are displayed in the picture | [5 empty] | Parameters
[6 empty] | heat capacity of water | 4180
[6 empty] | water density | 1000
[6 empty] | heat capacity of the rock | 820
[6 empty] | rock density | 2600
Eq. 23
Xcloud | 106.3988 | m
Eq. 24
Ycloud | 208.1798 | m
Note, the dimensions of the thermal cloud are determined based on numerical modeling of an idealized case. These should be significantly overestimated values, determined at a thermal gradient of 12°C. The boundaries are chosen lines where the thermal change compared to the original state is 1°C. If the gradient of the poured water was smaller, we cannot say how the boundaries will decrease or increase, only that the temperature change on the given line will be directly proportionally smaller. Such calculated values are never superior to more precise calculations as this is a very rough approximation.